## Complete Map
Fronius Datamanager Register Map: Integer Inverter Model (101, 102, 103)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
212 | 212 | 1 | RW | 0x03 0x06 0x10 | F_Delete_Data | Delete stored ratings of the current inverter by writing 0xFFFF. | uint16 |  |  | 0xFFFF
213 | 213 | 1 | RW | 0x03 0x06 0x10 | F_Store_Data | Rating data of all inverters connected to the Fronius Datamanager are persistently stored by writing 0xFFFF. | uint16 |  |  | 0xFFFF
214 | 214 | 1 | R | 0x03 | F_Active_State_Code | Current active state code of inverter - Description can be found in inverter manual | uint16 |  |  | not supported for Fronius Hybrid inverters (because of this inverter status maybe reported differently during nighttime compared to other inverter types)
215 | 215 | 1 | RW | 0x03 0x06 0x10 | F_Reset_All_Event_Flags | Write 0xFFFF to reset all event flags and active state code. | uint16 |  |  | 0xFFFF
216 | 216 | 1 | RW | 0x03 0x06 0x10 | F_ModelType | Type of SunSpec models used for inverter and meter data. Write 1 or 2 and then immediately 6 to acknowledge setting. | uint16 |  |  | 1: Floating point 2: Integer & SF
217 | 217 | 1 | RW | 0x03 0x06 0x10 | F_Storage_Restrictions_View_Mode | Type of Restrictions reported in BasicStorageControl Model (IC124). Local restrictions are those that are set by Modbus Interface. Global restrictions are those that are set system wide. | uint16 |  |  | 0: local (default); 1: global
500 | 501 | 2 | R | 0x03 | F_Site_Power | Total power (site sum) of all connected inverters. | uint32 | W
502 | 505 | 4 | R | 0x03 | F_Site_Energy_Day | Total energy for current day of all connected inverters. | uint64 | Wh
506 | 509 | 4 | R | 0x03 | F_Site_Energy_Year | Total energy for last year of all connected inverters. | uint64 | Wh
510 | 513 | 4 | R | 0x03 | F_Site_Energy_Total | Total energy of all connected inverters. | uint64 | Wh
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
40021 | 40036 | 16 | R | 0x03 | Md | Device model | String32 |  |  | z. B. IG+150V
40037 | 40044 | 8 | R | 0x03 | Opt | Options | String16 |  |  | Firmware version of Datamanager
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of inverter | String16
40053 | 40068 | 16 | R | 0x03 | SN | Serialnumber of the inverter | String32 |  |  | Inverter Serial Number Please note, that the inverter serial number is not supported on all devices and also depends on the internal inverter controller‘s production date and its Software-Version. If the inverter serial number is not supported, then two fallbacks are implemented that are still unique but may not match the inverter serial number printed on the nameplate: 1: serial of inverter controller (PMC) if supported 2: Unique ID (UID) of inverter controller For SYMOHYBRID Inverters the Inverter serial number is not supported and this register always contains one of the two implemented fallbacks. Please note further that due to startup timing issues or synchronization faults this field may change its value during operation from one option to another, eg.: At boottime only UID is available and after some time device information is synchronized then this field changes from UID to PMC or inverter serial number.
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Inverter Modbus Map; 101: single phase, 102: split phase, 103: three phase | uint16 |  |  | 101, 102, 103
40071 | 40071 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 50
40072 | 40072 | 1 | R | 0x03 | A | AC Total Current value | uint16 | A | A_SF
40073 | 40073 | 1 | R | 0x03 | AphA | AC Phase-A Current value | uint16 | A | A_SF
40074 | 40074 | 1 | R | 0x03 | AphB | AC Phase-B Current value | uint16 | A | A_SF
40075 | 40075 | 1 | R | 0x03 | AphC | AC Phase-C Current value | uint16 | A | A_SF
40076 | 40076 | 1 | R | 0x03 | A_SF | AC Current Scale factor | sunssf
40077 | 40077 | 1 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | uint16 | V | V_SF
40078 | 40078 | 1 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | uint16 | V | V_SF
40079 | 40079 | 1 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | uint16 | V | V_SF
40080 | 40080 | 1 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | uint16 | V | V_SF
40081 | 40081 | 1 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | uint16 | V | V_SF
40082 | 40082 | 1 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | uint16 | V | V_SF
40083 | 40083 | 1 | R | 0x03 | V_SF | AC Voltage Scale factor | sunssf
40084 | 40084 | 1 | R | 0x03 | W | AC Power value | int16 | W | W_SF
40085 | 40085 | 1 | R | 0x03 | W_SF | AC Power Scale factor | sunssf
40086 | 40086 | 1 | R | 0x03 | Hz | AC Frequency value | uint16 | Hz | Hz_SF
40087 | 40087 | 1 | R | 0x03 | Hz_SF | Scale factor | sunssf
40088 | 40088 | 1 | R | 0x03 | VA | Apparent Power | int16 | VA | VA_SF
40089 | 40089 | 1 | R | 0x03 | VA_SF | Scale factor | sunssf
40090 | 40090 | 1 | R | 0x03 | VAr | Reactive Power | int16 | VAr | VAr_SF
40091 | 40091 | 1 | R | 0x03 | VAr_SF | Scale factor | sunssf
40092 | 40092 | 1 | R | 0x03 | PF | Power Factor | int16 | % | PF_SF
40093 | 40093 | 1 | R | 0x03 | PF_SF | Scale factor | sunssf
40094 | 40095 | 2 | R | 0x03 | WH | AC Lifetime Energy production | uint32 | Wh | WH_SF | may be imprecise
40096 | 40096 | 1 | R | 0x03 | WH_SF | AC Lifetime Energy production scale factor | sunssf
40097 | 40097 | 1 | R | 0x03 | DCA | DC Current value | uint16 | A | DCA_SF | Not supported if multiple DC inputs; current can be found in Multiple MPPT model
40098 | 40098 | 1 | R | 0x03 | DCA_SF | Scale factor | sunssf |  |  | Not supported if multiple DC inputs.
40099 | 40099 | 1 | R | 0x03 | DCV | DC Voltage value | uint16 | V | DCV_SF | Not supported if multiple DC inputs; voltage can be found in Multiple MPPT model
40100 | 40100 | 1 | R | 0x03 | DCV_SF | Scale factor | sunssf |  |  | Not supported if multiple DC inputs.
40101 | 40101 | 1 | R | 0x03 | DCW | DC Power value | int16 | W | DCW_SF | Total power of all DC inputs
40102 | 40102 | 1 | R | 0x03 | DCW_SF | Scale factor | sunssf
40103 | 40103 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | ° C | Tmp_SF | Not supported
40104 | 40104 | 1 | R | 0x03 | TmpSnk | Coolant or Heat Sink Temperature | int16 | ° C | Tmp_SF | Not supported
40105 | 40105 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | ° C | Tmp_SF | Not supported
40106 | 40106 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | ° C | Tmp_SF | Not supported
40107 | 40107 | 1 | R | 0x03 | Tmp_SF | Scale factor | sunssf |  |  | Not supported
40108 | 40108 | 1 | R | 0x03 | St | Operating State | enum16 | Enumerated | N/A
40109 | 40109 | 1 | R | 0x03 | StVnd | Vendor Defined Operating State | enum16 | Enumerated | N/A
40110 | 40111 | 2 | R | 0x03 | Evt1 | Event Flags (bits 0-31) | uint32 | Bitfield | N/A
40112 | 40113 | 2 | R | 0x03 | Evt2 | Event Flags (bits 32-63) | uint32 | Bitfield | N/A
40114 | 40115 | 2 | R | 0x03 | EvtVnd1 | Vendor Defined Event Flags (bits 0-31) | uint32 | Bitfield | N/A
40116 | 40117 | 2 | R | 0x03 | EvtVnd2 | Vendor Defined Event Flags (bits 32-63) | uint32 | Bitfield | N/A
40118 | 40119 | 2 | R | 0x03 | EvtVnd3 | Vendor Defined Event Flags (bits 64-95) | uint32 | Bitfield | N/A
40120 | 40121 | 2 | R | 0x03 | EvtVnd4 | Vendor Defined Event Flags (bits 96-127) | uint32 | Bitfield | N/A
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40122 | 40122 | 1 | R | 0x03 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 |  |  | 120
40123 | 40123 | 1 | R | 0x03 | L | Length of Nameplate Model | uint16 | Registers |  | 26
40124 | 40124 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4
40125 | 40125 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
40126 | 40126 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 0
40127 | 40127 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
40128 | 40128 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 0
40129 | 40129 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
40130 | 40130 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | Not supported
40131 | 40131 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | Not supported
40132 | 40132 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
40133 | 40133 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
40134 | 40134 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
40135 | 40135 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
40136 | 40136 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF
40137 | 40137 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | Not supported
40138 | 40138 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | Not supported
40139 | 40139 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF
40140 | 40140 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
40141 | 40141 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
40142 | 40142 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | 0
40143 | 40143 | 1 | R | 0x03 | AhrRtg | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | Not supported
40144 | 40144 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | Not supported
40145 | 40145 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
40146 | 40146 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
40147 | 40147 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
40148 | 40148 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
40149 | 40149 | 1 | R | 0x03 | Pad | Pad register
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40150 | 40150 | 1 | R | 0x03 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 |  |  | 121
40151 | 40151 | 1 | R | 0x03 | L | Length of Basic Settings Model | uint16 | Registers |  | 30
40152 | 40152 | 1 | RW | 0x03 0x06 0x10 | WMax | Setting for maximum power output. Default to I_WRtg. | uint16 | W | Wmax_SF
40153 | 40153 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | Vref_SF
40154 | 40154 | 1 | RW | 0x03 0x06 0x10 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF
40155 | 40155 | 1 | RW | 0x03 0x06 0x10 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | Not supported
40156 | 40156 | 1 | RW | 0x03 0x06 0x10 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | Not supported
40157 | 40157 | 1 | RW | 0x03 | VAMax | Setpoint for maximum apparent power. Default to I_VARtg. | uint16 | VA | VAMax_SF
40158 | 40158 | 1 | R | 0x03 | VARMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VARMax_SF
40159 | 40159 | 1 | R | 0x03 | VARMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VARMax_SF | Not supported
40160 | 40160 | 1 | R | 0x03 | VARMaxQ3 | Setting for maximum reactive power in quadrant 3 Default to VArRtgQ3. | int16 | var | VARMax_SF | Not supported
40161 | 40161 | 1 | R | 0x03 | VARMaxQ4 | Setting for maximum reactive power in quadrant 4 Default to VArRtgQ4. | int16 | var | VARMax_SF
40162 | 40162 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/min | WGra_SF | Not supported
40163 | 40163 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF
40164 | 40164 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | Not supported
40165 | 40165 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | Not supported
40166 | 40166 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF
40167 | 40167 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | Not supported
40168 | 40168 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | Not supported
40169 | 40169 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | Not supported
40170 | 40170 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | Not supported
40171 | 40171 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | Not supported
40172 | 40172 | 1 | R | 0x03 | WMax_SF | Scale factor for maximum power output. | sunssf |  |  | 1
40173 | 40173 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
40174 | 40174 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
40175 | 40175 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | Not supported
40176 | 40176 | 1 | R | 0x03 | VAMax_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 1
40177 | 40177 | 1 | R | 0x03 | VARMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
40178 | 40178 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | Not supported
40179 | 40179 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
40180 | 40180 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | Not supported
40181 | 40181 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | Not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40182 | 40182 | 1 | R | 0x03 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 |  |  | 122
40183 | 40183 | 1 | R | 0x03 | L | Length of Measurements_Status Model | uint16 | Registers |  | 44
40184 | 40184 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating Bit 3: Test
40185 | 40185 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | bit 0: CONNECTED bit 1: AVAILABLE bit 2: OPERATING bit 3: TEST
40186 | 40186 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | 0: Disconnected 1: Connected
40187 | 40190 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
40191 | 40194 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | Not supported
40195 | 40198 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | Not supported
40199 | 40202 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | Not supported
40203 | 40206 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | Not supported
40207 | 40210 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | Not supported
40211 | 40211 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | Not supported
40212 | 40212 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | Not supported
40213 | 40213 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | W | WAval_SF | Not supported
40214 | 40214 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | Not supported
40215 | 40216 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. Bits are persistent and must be cleared by the controller. | bitfield32 |  |  | Not supported
40217 | 40218 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
40219 | 40222 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | String8 |  |  | RTC
40223 | 40224 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
40225 | 40225 | 1 | R | 0x03 | RtSt | Bit Mask indicating which voltage ride through modes are currently active. | bitfield16 |  |  | Not supported
40226 | 40226 | 1 | R | 0x03 | Ris | Isolation resistance | uint16 | Ohm | Ris_SF | Not supported
40227 | 40227 | 1 | R | 0x03 | Ris_SF | Scale factor for Isolation resistance | int16 |  |  | Not supported
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40228 | 40228 | 1 | R | 0x03 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 |  |  | 123
40229 | 40229 | 1 | R | 0x03 | L | Length of Immediate Controls Model | uint16 | Registers |  | 24
40230 | 40230 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs
40231 | 40231 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs
40232 | 40232 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | bitfield16 |  |  | 0: Disconnected 1: Connected
40233 | 40233 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF
40234 | 40234 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 – 300
40235 | 40235 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 – 28800
40236 | 40236 | 1 | RW | 0x03 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
40237 | 40237 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40238 | 40238 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | 0.8 to 1.0 and -0.8 to -0.999
40239 | 40239 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 – 300
40240 | 40240 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 – 28800
40241 | 40241 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
40242 | 40242 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40243 | 40243 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of I_WMax. | int16 | % WMax | VArWMaxPct_SF | not supported - reflects VarMaxPct
40244 | 40244 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of I_VArMax. | int16 | % VArMax | VArPct_SF
40245 | 40245 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of I_VArAval. | int16 | % VArAval | VArPct_SF | Not supported
40246 | 40246 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 – 300
40247 | 40247 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 – 28800
40248 | 40248 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
40249 | 40249 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
40250 | 40250 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Fixed VAR enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
40251 | 40251 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
40252 | 40252 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
40253 | 40253 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power. | sunssf |  |  | 0
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40254 | 40254 | 1 | R | 0x03 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Mode | unit16 |  |  | 160
40255 | 40255 | 1 | R | 0x03 | L | Length of Multiple MPPT Inverter Extension Model | uint16 |  |  | 48
40256 | 40256 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf
40257 | 40257 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf
40258 | 40258 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf
40259 | 40259 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | Not supported for Fronius Hybrid inverters
40260 | 40261 | 2 | R | 0x03 | Evt | Global Events | bitfield32
40262 | 40262 | 1 | R | 0x03 | N | Number of Modules | uint16 |  |  | 2
40263 | 40263 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | Not supported
40264 | 40264 | 1 | R | 0x03 | 1_ID | Input ID | uint16 |  |  | 1
40265 | 40272 | 8 | R | 0x03 | 1_IDStr | Input ID Sting | String16 |  |  | "String 1"
40273 | 40273 | 1 | R | 0x03 | 1_DCA | DC Current | uint16 | A | DCA_SF
40274 | 40274 | 1 | R | 0x03 | 1_DCV | DC Voltage | uint16 | V | DCV_SF
40275 | 40275 | 1 | R | 0x03 | 1_DCW | DC Power | uint16 | W | DCW_SF
40276 | 40277 | 2 | R | 0x03 | 1_DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | Not supported for Fronius Hybrid inverters
40278 | 40279 | 2 | R | 0x03 | 1_Tms | Timestamp | uint32 | Secs
40280 | 40280 | 1 | R | 0x03 | 1_Tmp | Temperature | int16 | C
40281 | 40281 | 1 | R | 0x03 | 1_DCSt | Operating State | enum16
40282 | 40283 | 2 | R | 0x03 | 1_DCEvt | Module Events | bitfield32
40284 | 40284 | 1 | R | 0x03 | 2_ID | Input ID | uint16 |  |  | 2
40285 | 40292 | 8 | R | 0x03 | 2_IDStr | Input ID Sting | String16 |  |  | "String 2" or "Not supported"
40293 | 40293 | 1 | R | 0x03 | 2_DCA | DC Current | uint16 | A | DCA_SF | Not supported if only one DC input.
40294 | 40294 | 1 | R | 0x03 | 2_DCV | DC Voltage | uint16 | V | DCV_SF | Not supported if only one DC input.
40295 | 40295 | 1 | R | 0x03 | 2_DCW | DC Power | uint16 | W | DCW_SF | Not supported if only one DC input.
40296 | 40297 | 2 | R | 0x03 | 2_DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | Not supported if only one DC input. Not supported for Fronius Hybrid inverters
40298 | 40299 | 2 | R | 0x03 | 2_Tms | Timestamp | uint32 | Secs |  | Not supported if only one DC input.
40300 | 40300 | 1 | R | 0x03 | 2_Tmp | Temperature | int16 | C |  | Not supported if only one DC input.
40301 | 40301 | 1 | R | 0x03 | 2_DCSt | Operating State | enum16 |  |  | Not supported if only one DC input.
40302 | 40303 | 2 | R | 0x03 | 2_DCEvt | Module Events | bitfield32 |  |  | Not supported if only one DC input.
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40304 | 40304 | 1 | R | 0x03 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Basic Storage Controls Model | uint16 |  |  | 124
40305 | 40305 | 1 | R | 0x03 | L | Length of Basic Storage Controls | uint16 | Registers |  | 24
40306 | 40306 | 1 | R | 0x03 | WchaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only. | uint16 | W | WChaMax_SF
40307 | 40307 | 1 | R | 0x03 | WchaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100
40308 | 40308 | 1 | R | 0x03 | WdisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100
40309 | 40309 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. Bitfield value. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
40310 | 40310 | 1 | R | 0x03 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF | Not supported
40311 | 40311 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
40312 | 40312 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
40313 | 40313 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | Not supported
40314 | 40314 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | Not supported
40315 | 40315 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
40316 | 40316 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and wChaMax defines max. Discharge rate. See wChaMax for details. | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will be silently ignored by the inverter. Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40317 | 40317 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and wChaMax defines max. Charge rate. See wChaMax for details. | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will be silently ignored by the inverter. Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
40318 | 40318 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | Not supported
40319 | 40319 | 1 | R | 0x03 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | Not supported
40320 | 40320 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | Not supported
40321 | 40321 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet | Setpoint to enable/disable charging from grid | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
40322 | 40322 | 1 | R | 0x03 | WchaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
40323 | 40323 | 1 | R | 0x03 | WchaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
40324 | 40324 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | Not supported
40325 | 40325 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
40326 | 40326 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
40327 | 40327 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | Not supported
40328 | 40328 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | Not supported
40329 | 40329 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40330 | 40330 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40331 | 40331 | 1 | R | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## C001 Common
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 2 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
3 | 3 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a SunSpec Common Model block | uint16 |  |  | 1
4 | 4 | 1 | R | 0x03 | L | Length of Common Model block | uint16 | Registers |  | 65
5 | 20 | 16 | R | 0x03 | Mn | Manufacturer | String32 |  |  | Fronius
21 | 36 | 16 | R | 0x03 | Md | Device model | String32 |  |  | z. B. IG+150V [3p]
37 | 44 | 8 | R | 0x03 | Opt | Options | String16 |  |  | Firmware version of Datamanager
45 | 52 | 8 | R | 0x03 | Vr | SW version of inverter | String16
53 | 68 | 16 | R | 0x03 | SN | Serialnumber of the inverter | String32 |  |  | Inverter Serial Number Please note, that the inverter serial number is not supported on all devices and also depends on the internal inverter controller‘s production date and its Software-Version. If the inverter serial number is not supported, then two fallbacks are implemented that are still unique but may not match the inverter serial number printed on the nameplate: 1: serial of inverter controller (PMC) if supported 2: Unique ID (UID) of inverter controller For SYMOHYBRID Inverters the Inverter serial number is not supported and this register always contains one of the two implemented fallbacks. Please note further that due to startup timing issues or synchronization faults this field may change its value during operation from one option to another, eg.: At boottime only UID is available and after some time device information is synchronized then this field changes from UID to PMC or inverter serial number.
69 | 69 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## I10X Inverter
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Uniquely identifies this as a SunSpec Inverter Modbus Map; 101: single phase, 102: split phase, 103: three phase | uint16 |  |  | 101, 102, 103
2 | 2 | 1 | R | 0x03 | L | Length of inverter model block | uint16 | Registers |  | 50
3 | 3 | 1 | R | 0x03 | A | AC Total Current value | uint16 | A | A_SF
4 | 4 | 1 | R | 0x03 | AphA | AC Phase-A Current value | uint16 | A | A_SF
5 | 5 | 1 | R | 0x03 | AphB | AC Phase-B Current value | uint16 | A | A_SF
6 | 6 | 1 | R | 0x03 | AphC | AC Phase-C Current value | uint16 | A | A_SF
7 | 7 | 1 | R | 0x03 | A_SF | AC Current Scale factor | sunssf
8 | 8 | 1 | R | 0x03 | PPVphAB | AC Voltage Phase-AB value | uint16 | V | V_SF
9 | 9 | 1 | R | 0x03 | PPVphBC | AC Voltage Phase-BC value | uint16 | V | V_SF
10 | 10 | 1 | R | 0x03 | PPVphCA | AC Voltage Phase-CA value | uint16 | V | V_SF
11 | 11 | 1 | R | 0x03 | PhVphA | AC Voltage Phase-A-to-neutral value | uint16 | V | V_SF
12 | 12 | 1 | R | 0x03 | PhVphB | AC Voltage Phase-B-to-neutral value | uint16 | V | V_SF
13 | 13 | 1 | R | 0x03 | PhVphC | AC Voltage Phase-C-to-neutral value | uint16 | V | V_SF
14 | 14 | 1 | R | 0x03 | V_SF | AC Voltage Scale factor | sunssf
15 | 15 | 1 | R | 0x03 | W | AC Power value | int16 | W | W_SF
16 | 16 | 1 | R | 0x03 | W_SF | AC Power Scale factor | sunssf
17 | 17 | 1 | R | 0x03 | Hz | AC Frequency value | uint16 | Hz | Hz_SF
18 | 18 | 1 | R | 0x03 | Hz_SF | Scale factor | sunssf
19 | 19 | 1 | R | 0x03 | VA | Apparent Power | int16 | VA | VA_SF
20 | 20 | 1 | R | 0x03 | VA_SF | Scale factor | sunssf
21 | 21 | 1 | R | 0x03 | VAr | Reactive Power | int16 | VAr | VAr_SF
22 | 22 | 1 | R | 0x03 | VAr_SF | Scale factor | sunssf
23 | 23 | 1 | R | 0x03 | PF | Power Factor | int16 | % | PF_SF
24 | 24 | 1 | R | 0x03 | PF_SF | Scale factor | sunssf
25 | 26 | 2 | R | 0x03 | WH | AC Lifetime Energy production | uint32 | Wh | WH_SF | may be imprecise
27 | 27 | 1 | R | 0x03 | WH_SF | AC Lifetime Energy production scale factor | sunssf
28 | 28 | 1 | R | 0x03 | DCA | DC Current value | uint16 | A | DCA_SF | Not supported if multiple DC inputs; current can be found in Multiple MPPT model
29 | 29 | 1 | R | 0x03 | DCA_SF | Scale factor | sunssf |  |  | Not supported if multiple DC inputs.
30 | 30 | 1 | R | 0x03 | DCV | DC Voltage value | uint16 | V | DCV_SF | Not supported if multiple DC inputs; voltage can be found in Multiple MPPT model
31 | 31 | 1 | R | 0x03 | DCV_SF | Scale factor | sunssf |  |  | Not supported if multiple DC inputs.
32 | 32 | 1 | R | 0x03 | DCW | DC Power value | int16 | W | DCW_SF | Total power of all DC inputs
33 | 33 | 1 | R | 0x03 | DCW_SF | Scale factor | sunssf
34 | 34 | 1 | R | 0x03 | TmpCab | Cabinet Temperature | int16 | ° C | Tmp_SF | Not supported
35 | 35 | 1 | R | 0x03 | TmpSnk | Coolant or Heat Sink Temperature | int16 | ° C | Tmp_SF | Not supported
36 | 36 | 1 | R | 0x03 | TmpTrns | Transformer Temperature | int16 | ° C | Tmp_SF | Not supported
37 | 37 | 1 | R | 0x03 | TmpOt | Other Temperature | int16 | ° C | Tmp_SF | Not supported
38 | 38 | 1 | R | 0x03 | Tmp_SF | Scale factor | sunssf |  |  | Not supported
39 | 39 | 1 | R | 0x03 | St | Operating State | enum16 | Enumerated | N/A
40 | 40 | 1 | R | 0x03 | StVnd | Vendor Defined Operating State | enum16 | Enumerated | N/A
41 | 42 | 2 | R | 0x03 | Evt1 | Event Flags (bits 0-31) | uint32 | Bitfield | N/A
43 | 44 | 2 | R | 0x03 | Evt2 | Event Flags (bits 32-63) | uint32 | Bitfield | N/A
45 | 46 | 2 | R | 0x03 | EvtVnd1 | Vendor Defined Event Flags (bits 0-31) | uint32 | Bitfield | N/A
47 | 48 | 2 | R | 0x03 | EvtVnd2 | Vendor Defined Event Flags (bits 32-63) | uint32 | Bitfield | N/A
49 | 50 | 2 | R | 0x03 | EvtVnd3 | Vendor Defined Event Flags (bits 64-95) | uint32 | Bitfield | N/A
51 | 52 | 2 | R | 0x03 | EvtVnd4 | Vendor Defined Event Flags (bits 96-127) | uint32 | Bitfield | N/A

## I120 Nameplate
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 |  |  | 120
2 | 2 | 1 | R | 0x03 | L | Length of Nameplate Model | uint16 | Registers |  | 26
3 | 3 | 1 | R | 0x03 | DERTyp | Type of DER device. Default value is 4 to indicate PV device. | enum16 |  |  | 4
4 | 4 | 1 | R | 0x03 | WRtg | Continuous power output capability of the inverter. | uint16 | W | WRtg_SF
5 | 5 | 1 | R | 0x03 | WRtg_SF | Scale factor | sunssf |  |  | 0
6 | 6 | 1 | R | 0x03 | VARtg | Continuous Volt-Ampere capability of the inverter. | uint16 | VA | VARtg_SF
7 | 7 | 1 | R | 0x03 | VARtg_SF | Scale factor | sunssf |  |  | 0
8 | 8 | 1 | R | 0x03 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1. | int16 | var | VArRtg_SF
9 | 9 | 1 | R | 0x03 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2. | int16 | var | VArRtg_SF | Not supported
10 | 10 | 1 | R | 0x03 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3. | int16 | var | VArRtg_SF | Not supported
11 | 11 | 1 | R | 0x03 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4. | int16 | var | VArRtg_SF
12 | 12 | 1 | R | 0x03 | VArRtg_SF | Scale factor | sunssf |  |  | 1
13 | 13 | 1 | R | 0x03 | ARtg | Maximum RMS AC current level capability of the inverter. | uint16 | A | ARtg_SF
14 | 14 | 1 | R | 0x03 | ARtg_SF | Scale factor | sunssf |  |  | -2
15 | 15 | 1 | R | 0x03 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1. | int16 | cos() | PFRtg_SF
16 | 16 | 1 | R | 0x03 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2. | int16 | cos() | PFRtg_SF | Not supported
17 | 17 | 1 | R | 0x03 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3. | int16 | cos() | PFRtg_SF | Not supported
18 | 18 | 1 | R | 0x03 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4. | int16 | cos() | PFRtg_SF
19 | 19 | 1 | R | 0x03 | PFRtg_SF | Scale factor | sunssf |  |  | -3
20 | 20 | 1 | R | 0x03 | WHRtg | Nominal energy rating of storage device. | uint16 | Wh | WHRtg_SF
21 | 21 | 1 | R | 0x03 | WHRtg_SF | Scale factor | sunssf |  |  | 0
22 | 22 | 1 | R | 0x03 | AhrRtg | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating). | uint16 | AH | AhrRtg_SF | Not supported
23 | 23 | 1 | R | 0x03 | AhrRtg_SF | Scale factor for amp-hour rating. | sunssf |  |  | Not supported
24 | 24 | 1 | R | 0x03 | MaxChaRte | Maximum rate of energy transfer into the storage device. | uint16 | W | MaxChaRte_SF
25 | 25 | 1 | R | 0x03 | MaxChaRte_SF | Scale factor | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device. | uint16 | W | MaxDisChaRte_SF
27 | 27 | 1 | R | 0x03 | MaxDisChaRte_SF | Scale factor | sunssf |  |  | 0
28 | 28 | 1 | R | 0x03 | Pad | Pad register

## I121 Basic
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 |  |  | 121
2 | 2 | 1 | R | 0x03 | L | Length of Basic Settings Model | uint16 | Registers |  | 30
3 | 3 | 1 | RW | 0x03 0x06 0x10 | WMax | Setting for maximum power output. Default to I_WRtg. | uint16 | W | Wmax_SF
4 | 4 | 1 | R | 0x03 | VRef | Voltage at the PCC. | uint16 | V | VRef_SF
5 | 5 | 1 | RW | 0x03 0x06 0x10 | VRefOfs | Offset from PCC to inverter. | int16 | V | VRefOfs_SF
6 | 6 | 1 | RW | 0x03 0x06 0x10 | VMax | Setpoint for maximum voltage. | uint16 | V | VMinMax_SF | Not supported
7 | 7 | 1 | RW | 0x03 0x06 0x10 | VMin | Setpoint for minimum voltage. | uint16 | V | VMinMax_SF | Not supported
8 | 8 | 1 | R | 0x03 | VAMax | Setpoint for maximum apparent power. Default to I_VARtg. | int16 | VA | VAMax_SF
9 | 9 | 1 | R | 0x03 | VARMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | int16 | var | VARMax_SF
10 | 10 | 1 | R | 0x03 | VARMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | int16 | var | VARMax_SF | Not supported
11 | 11 | 1 | R | 0x03 | VARMaxQ3 | Setting for maximum reactive power in quadrant 3 Default to VArRtgQ3. | int16 | var | VARMax_SF | Not supported
12 | 12 | 1 | R | 0x03 | VARMaxQ4 | Setting for maximum reactive power in quadrant 4 Default to VArRtgQ4. | int16 | var | VARMax_SF
13 | 13 | 1 | R | 0x03 | WGra | Default ramp rate of change of active power due to command or internal action. | uint16 | % WMax/min | WGra_SF | Not supported
14 | 14 | 1 | R | 0x03 | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1. | int16 | cos() | PFMin_SF
15 | 15 | 1 | R | 0x03 | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2. | int16 | cos() | PFMin_SF | Not supported
16 | 16 | 1 | R | 0x03 | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3. | int16 | cos() | PFMin_SF | Not supported
17 | 17 | 1 | R | 0x03 | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4. | int16 | cos() | PFMin_SF
18 | 18 | 1 | R | 0x03 | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization. | enum16 |  |  | Not supported
19 | 19 | 1 | R | 0x03 | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic. | enum16 |  |  | Not supported
20 | 20 | 1 | R | 0x03 | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation. | uint16 | % WGra | MaxRmpRte_SF | Not supported
21 | 21 | 1 | R | 0x03 | ECPNomHz | Setpoint for nominal frequency at the ECP. | uint16 | Hz | ECPNomHz_SF | Not supported
22 | 22 | 1 | R | 0x03 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3. | enum16 |  |  | Not supported
23 | 23 | 1 | R | 0x03 | WMax_SF | Scale factor for maximum power output. | sunssf |  |  | 1
24 | 24 | 1 | R | 0x03 | VRef_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 0
25 | 25 | 1 | R | 0x03 | VRefOfs_SF | Scale factor for offset voltage. | sunssf |  |  | 0
26 | 26 | 1 | R | 0x03 | VMinMax_SF | Scale factor for min/max voltages. | sunssf |  |  | Not supported
27 | 27 | 1 | R | 0x03 | VAMax_SF | Scale factor for voltage at the PCC. | sunssf |  |  | 1
28 | 28 | 1 | R | 0x03 | VARMax_SF | Scale factor for reactive power. | sunssf |  |  | 1
29 | 29 | 1 | R | 0x03 | WGra_SF | Scale factor for default ramp rate. | sunssf |  |  | Not supported
30 | 30 | 1 | R | 0x03 | PFMin_SF | Scale factor for minimum power factor. | sunssf |  |  | -3
31 | 31 | 1 | R | 0x03 | MaxRmpRte_SF | Scale factor for maximum ramp percentage. | sunssf |  |  | Not supported
32 | 32 | 1 | R | 0x03 | ECPNomHz_SF | Scale factor for nominal frequency. | sunssf |  |  | Not supported

## I122 Extended
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 |  |  | 122
2 | 2 | 1 | R | 0x03 | L | Length of Measurements_Status Model | uint16 | Registers |  | 44
3 | 3 | 1 | R | 0x03 | PVConn | PV inverter present/available status. Enumerated value. | bitfield16 |  |  | Bit 0: Connected Bit 1: Available Bit 2: Operating Bit 3: Test
4 | 4 | 1 | R | 0x03 | StorConn | Storage inverter present/available status. Enumerated value. | bitfield16 |  |  | bit 0: CONNECTED bit 1: AVAILABLE bit 2: OPERATING bit 3: TEST
5 | 5 | 1 | R | 0x03 | ECPConn | ECP connection status: disconnected=0 connected=1. | bitfield16 |  |  | 0: Disconnected 1: Connected
6 | 9 | 4 | R | 0x03 | ActWh | AC lifetime active (real) energy output. | acc64 | Wh
10 | 13 | 4 | R | 0x03 | ActVAh | AC lifetime apparent energy output. | acc64 | VAh |  | Not supported
14 | 17 | 4 | R | 0x03 | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1. | acc64 | varh |  | Not supported
18 | 21 | 4 | R | 0x03 | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2. | acc64 | varh |  | Not supported
22 | 25 | 4 | R | 0x03 | ActVArhQ3 | AC lifetime negative energy output in quadrant 3. | acc64 | varh |  | Not supported
26 | 29 | 4 | R | 0x03 | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4. | acc64 | varh |  | Not supported
30 | 30 | 1 | R | 0x03 | VArAval | Amount of VARs available without impacting watts output. | int16 | var | VArAval_SF | Not supported
31 | 31 | 1 | R | 0x03 | VArAval_SF | Scale factor for available VARs. | sunssf |  |  | Not supported
32 | 32 | 1 | R | 0x03 | WAval | Amount of Watts available. | uint16 | W | WAval_SF | Not supported
33 | 33 | 1 | R | 0x03 | WAval_SF | Scale factor for available Watts. | sunssf |  |  | Not supported
34 | 35 | 2 | R | 0x03 | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached. Bits are persistent and must be cleared by the controller. | bitfield32 |  |  | Not supported
36 | 37 | 2 | R | 0x03 | StActCtl | Bit Mask indicating which inverter controls are currently active. | bitfield32 |  |  | Bit 0: FixedW Bit 1: FixedVAR Bit 2: FixedPF
38 | 41 | 4 | R | 0x03 | TmSrc | Source of time synchronization. | String8 |  |  | RTC
42 | 43 | 2 | R | 0x03 | Tms | Seconds since 01-01-2000 00:00 UTC | uint32 | Secs
44 | 44 | 1 | R | 0x03 | RtSt | Bit Mask indicating which voltage ride through modes are currently active. | bitfield16 |  |  | Not supported
45 | 45 | 1 | R | 0x03 | Riso | Isolation resistance | uint16 | Ohm | Riso_SF | Not supported
46 | 46 | 1 | R | 0x03 | Riso_SF | Scale factor for Isolation resistance | int16 |  |  | Not supported

## I123 Immediate
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 |  |  | 123
2 | 2 | 1 | R | 0x03 | L | Length of Immediate Controls Model | uint16 | Registers |  | 24
3 | 3 | 1 | RW | 0x03 0x06 0x10 | Conn_WinTms | Time window for connect/disconnect. | uint16 | Secs
4 | 4 | 1 | RW | 0x03 0x06 0x10 | Conn_RvrtTms | Timeout period for connect/disconnect. | uint16 | Secs
5 | 5 | 1 | RW | 0x03 0x06 0x10 | Conn | Enumerated valued. Connection control. | bitfield16 |  |  | 0: Disconnected 1: Connected
6 | 6 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct | Set power output to specified level. | uint16 | % WMax | WMaxLimPct_SF
7 | 7 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_WinTms | Time window for power limit change. | uint16 | Secs |  | 0 - 300
8 | 8 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RvrtTms | Timeout period for power limit. | uint16 | Secs |  | 0 - 28800
9 | 9 | 1 | RW | 0x03 0x06 0x10 | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
10 | 10 | 1 | RW | 0x03 0x06 0x10 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
11 | 11 | 1 | RW | 0x03 0x06 0x10 | OutPFSet | Set power factor to specific value - cosine of angle. | int16 | cos() | OutPFSet_SF | 0.8 to 1.0 and -0.8 to -0.999
12 | 12 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_WinTms | Time window for power factor change. | uint16 | Secs |  | 0 – 300
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RvrtTms | Timeout period for power factor. | uint16 | Secs |  | 0 – 28800
14 | 14 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
15 | 15 | 1 | RW | 0x03 0x06 0x10 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
16 | 16 | 1 | R | 0x03 | VArWMaxPct | Reactive power in percent of I_WMax. | int16 | % WMax | VArWMaxPct_SF | not supported - reflects VarMaxPct
17 | 17 | 1 | RW | 0x03 0x06 0x10 | VArMaxPct | Reactive power in percent of I_VArMax. | int16 | % VArMax | VArPct_SF
18 | 18 | 1 | R | 0x03 | VArAvalPct | Reactive power in percent of I_VArAval. | int16 | % VArAval | VArPct_SF | Not supported
19 | 19 | 1 | RW | 0x03 0x06 0x10 | VArPct_WinTms | Time window for VAR limit change. | uint16 | Secs |  | 0 – 300
20 | 20 | 1 | RW | 0x03 0x06 0x10 | VArPct_RvrtTms | Timeout period for VAR limit. | uint16 | Secs |  | 0 – 28800
21 | 21 | 1 | RW | 0x03 0x06 0x10 | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | 0 - 65534 (0xFFFF has the same effect as 0x0000)
22 | 22 | 1 | R | 0x03 | VArPct_Mod | Enumerated value. VAR limit mode. | enum16 |  |  | 2: VAR limit as a % of VArMax
23 | 23 | 1 | RW | 0x03 0x06 0x10 | VArPct_Ena | Enumerated valued. Fixed VAR enable/disable control. | enum16 |  |  | 0: Disabled 1: Enabled
24 | 24 | 1 | R | 0x03 | WMaxLimPct_SF | Scale factor for power output percent. | sunssf |  |  | -2
25 | 25 | 1 | R | 0x03 | OutPFSet_SF | Scale factor for power factor. | sunssf |  |  | -3
26 | 26 | 1 | R | 0x03 | VArPct_SF | Scale factor for reactive power. | sunssf |  |  | 0

## I160 MultiMPPT
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Mode | unit16 |  |  | 160
2 | 2 | 1 | R | 0x03 | L | Length of Multiple MPPT Inverter Extension Model | uint16 |  |  | 48
3 | 3 | 1 | R | 0x03 | DCA_SF | Current Scale Factor | sunssf
4 | 4 | 1 | R | 0x03 | DCV_SF | Voltage Scale Factor | sunssf
5 | 5 | 1 | R | 0x03 | DCW_SF | Power Scale Factor | sunssf
6 | 6 | 1 | R | 0x03 | DCWH_SF | Energy Scale Factor | sunssf |  |  | Not supported for Fronius Hybrid inverters
7 | 8 | 2 | R | 0x03 | Evt | Global Events | bitfield32
9 | 9 | 1 | R | 0x03 | N | Number of Modules | uint16 |  |  | 2
10 | 10 | 1 | R | 0x03 | TmsPer | Timestamp Period | uint16 |  |  | Not supported
11 | 11 | 1 | R | 0x03 | 1_ID | Input ID | uint16 |  |  | 1
12 | 19 | 8 | R | 0x03 | 1_IDStr | Input ID Sting | String16 |  |  | "String 1"
20 | 20 | 1 | R | 0x03 | 1_DCA | DC Current | uint16 | A | DCA_SF
21 | 21 | 1 | R | 0x03 | 1_DCV | DC Voltage | uint16 | V | DCV_SF
22 | 22 | 1 | R | 0x03 | 1_DCW | DC Power | uint16 | W | DCW_SF
23 | 24 | 2 | R | 0x03 | 1_DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | Not supported for Fronius Hybrid inverters
25 | 26 | 2 | R | 0x03 | 1_Tms | Timestamp | uint32 | Secs
27 | 27 | 1 | R | 0x03 | 1_Tmp | Temperature | int16 | C
28 | 28 | 1 | R | 0x03 | 1_DCSt | Operating State | enum16
29 | 30 | 2 | R | 0x03 | 1_DCEvt | Module Events | bitfield32
31 | 31 | 1 | R | 0x03 | 2_ID | Input ID | uint16 |  |  | 2
32 | 39 | 8 | R | 0x03 | 2_IDStr | Input ID Sting | String16 |  |  | "String 2" or "Not supported"
40 | 40 | 1 | R | 0x03 | 2_DCA | DC Current | uint16 | A | DCA_SF | Not supported if only one DC input.
41 | 41 | 1 | R | 0x03 | 2_DCV | DC Voltage | uint16 | V | DCV_SF | Not supported if only one DC input.
42 | 42 | 1 | R | 0x03 | 2_DCW | DC Power | uint16 | W | DCW_SF | Not supported if only one DC input.
43 | 44 | 2 | R | 0x03 | 2_DCWH | Lifetime Energy | acc32 | Wh | DCWH_SF | Not supported if only one DC input. Not supported for Fronius Hybrid inverters
45 | 46 | 2 | R | 0x03 | 2_Tms | Timestamp | uint32 | Secs |  | Not supported if only one DC input.
47 | 47 | 1 | R | 0x03 | 2_Tmp | Temperature | int16 | C |  | Not supported if only one DC input.
48 | 48 | 1 | R | 0x03 | 2_DCSt | Operating State | enum16 |  |  | Not supported if only one DC input.
49 | 50 | 2 | R | 0x03 | 2_DCEvt | Module Events | bitfield32 |  |  | Not supported if only one DC input.

## IC124 Basic Storage Control
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Basic Storage Controls Model | uint16 |  |  | 124
2 | 2 | 1 | R | 0x03 | L | Length of Basic Storage Controls | uint16 | Registers |  | 24
3 | 3 | 1 | R | 0x03 | WchaMax | Setpoint for maximum charge. Additional Fronius description: Reference Value for maximum Charge and Discharge. Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. Every rate between this two limits is allowed. Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only. | uint16 | W | WChaMax_SF
4 | 4 | 1 | R | 0x03 | WchaGra | Setpoint for maximum charging rate. Default is MaxChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100
5 | 5 | 1 | R | 0x03 | WdisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte. | uint16 | % WChaMax/sec | WChaDisChaGra_SF | 100
6 | 6 | 1 | RW | 0x03 0x06 0x10 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value. Additional Fronius description: Active hold/discharge/charge storage control mode. Set the charge field to enable charging and the discharge field to enable discharging. Bitfield value. | bitfield16 |  |  | bit 0: CHARGE bit 1: DiSCHARGE
7 | 7 | 1 | R | 0x03 | VAChaMax | Setpoint for maximum charging VA. | uint16 | VA | VAChaMax_SF | Not supported
8 | 8 | 1 | RW | 0x03 0x06 0x10 | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. | uint16 | % WChaMax | MinRsvPct_SF
9 | 9 | 1 | R | 0x03 | ChaState | Currently available energy as a percent of the capacity rating. | uint16 | % AhrRtg | ChaState_SF
10 | 10 | 1 | R | 0x03 | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg). | uint16 | AH | StorAval_SF | Not supported
11 | 11 | 1 | R | 0x03 | InBatV | Internal battery voltage. | uint16 | V | InBatV_SF | Not supported
12 | 12 | 1 | R | 0x03 | ChaSt | Charge status of storage device. Enumerated value. | enum16 |  |  | 1: OFF 2: EMPTY 3: DISCHAGING 4: CHARGING 5: FULL 6: HOLDING 7: TESTING The status TESTING is used during battery calibration or service charge.
13 | 13 | 1 | RW | 0x03 0x06 0x10 | OutWRte | Percent of max discharge rate. Additional Fronius description: Defines maximum Discharge rate. If not used than the default is 100 and wChaMax defines max. Discharge rate. See wChaMax for details. | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will be silently ignored by the inverter. Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
14 | 14 | 1 | RW | 0x03 0x06 0x10 | InWRte | Percent of max charging rate. Additional Fronius description: Defines maximum Charge rate. If not used than the default is 100 and wChaMax defines max. Charge rate. See wChaMax for details. | int16 | % WChaMax | InOutWRte_SF | valid range -100.00% - +100.00% Please note that this register has a scale factor in Register InOutWRte_SF, so for InOutWRte_SF = -2 the valid range in raw values is from -10000 to 10000. Please be aware that setting an invalid power window will be silently ignored by the inverter. Invalid power windows are all windows where condition: ((StorCtl_Mod == 3) AND ((-1) * InWRtg > OutWRtg)) evaluates to true. This can happen for example if two negative values are written into InWRtg and OutWRtg and both limits are activated by StorCtl_Mod = 3.
15 | 15 | 1 | R | 0x03 | InOutWRte_WinTms | Time window for charge/discharge rate change. | uint16 | Secs |  | Not supported
16 | 16 | 1 | R | 0x03 | InOutWRte_RvrtTms | Timeout period for charge/discharge rate. | uint16 | Secs |  | Not supported
17 | 17 | 1 | R | 0x03 | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint. | uint16 | Secs |  | Not supported
18 | 18 | 1 | RW | 0x03 0x06 0x10 | ChaGriSet | Setpoint to enable/disable charging from grid | enum16 |  |  | 0: PV (Charging from grid disabled) 1: GRID (Charging from grid enabled)
19 | 19 | 1 | R | 0x03 | WchaMax_SF | Scale factor for maximum charge. | sunssf |  |  | 0
20 | 20 | 1 | R | 0x03 | WchaDisChaGra_SF | Scale factor for maximum charge and discharge rate. | sunssf |  |  | 0
21 | 21 | 1 | R | 0x03 | VAChaMax_SF | Scale factor for maximum charging VA. | sunssf |  |  | Not supported
22 | 22 | 1 | R | 0x03 | MinRsvPct_SF | Scale factor for minimum reserve percentage. | sunssf |  |  | -2
23 | 23 | 1 | R | 0x03 | ChaState_SF | Scale factor for available energy percent. | sunssf |  |  | -2
24 | 24 | 1 | R | 0x03 | StorAval_SF | Scale factor for state of charge. | sunssf |  |  | Not supported
25 | 25 | 1 | R | 0x03 | InBatV_SF | Scale factor for battery voltage. | sunssf |  |  | Not supported
26 | 26 | 1 | R | 0x03 | InOutWRte_SF | Scale factor for percent charge/discharge rate. | sunssf |  |  | -2

## End Block
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | RO | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | RO | 0x03 | L | Length of model block | uint16 | Registers |  | 0

## Fronius Register
Start Offset | End Offset | Size | RW | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
212 | 212 | 1 | RW | 0x03 0x06 0x10 | F_Delete_Data | Delete stored ratings of the current inverter by writing 0xFFFF. | uint16 |  |  | 0xFFFF
213 | 213 | 1 | RW | 0x03 0x06 0x10 | F_Store_Data | Rating data of all inverters connected to the Fronius Datamanager are persistently stored by writing 0xFFFF. | uint16 |  |  | 0xFFFF
214 | 214 | 1 | R | 0x03 | F_Active_State_Code | Current active state code of inverter - Description can be found in inverter manual | uint16
215 | 215 | 1 | RW | 0x03 0x06 0x10 | F_Reset_All_Event_Flags | Write 0xFFFF to reset all event flags and active state code. | uint16 |  |  | 0xFFFF
216 | 216 | 1 | RW | 0x03 0x06 0x10 | F_ModelType | Type of SunSpec models used for inverter and meter data. Write 1 or 2 and then immediately 6 to acknowledge setting. | uint16 |  |  | 1: Floating point 2: Integer & SF
217 | 217 | 1 | RW | 0x03 0x06 0x10 | F_Storage_Restrictions_View_Mode | Type of Restrictions reported in BasicStorageControl Model (IC124). Local restrictions are those that are set by Modbus Interface. Global restrictions are those that are set system wide. | uint16 |  |  | 0: local (default); 1: global
500 | 501 | 2 | R | 0x03 | F_Site_Power | Total power (site sum) of all connected inverters. | uint32 | W
502 | 505 | 4 | R | 0x03 | F_Site_Energy_Day | Total energy for current day of all connected inverters. | uint64 | Wh
506 | 509 | 4 | R | 0x03 | F_Site_Energy_Year | Total energy for last year of all connected inverters. | uint64 | Wh
510 | 513 | 4 | R | 0x03 | F_Site_Energy_Total | Total energy of all connected inverters. | uint64 | Wh