## Complete Map
Smart Meter Register Map with Float AC-Meter Model
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40001 | 40002 | 2 | R | 0x03 | SID | Well-known value. Uniquely identifies this as a SunSpec Modbus Map | uint32 |  |  | 0x53756e53 ('SunS')
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40003 | 40003 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
40004 | 40004 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
40005 | 40020 | 16 | R | 0x03 | Mn | Smart Meter Manufacturer | string |  |  | e.g. "Fronius"
40021 | 40036 | 16 | R | 0x03 | Md | Smart Meter Model | string |  |  | e.g. "Smart Meter 63A"
40037 | 40044 | 8 | R | 0x03 | Opt | Smart Meter Name | string |  |  | e.g. "<primary>"
40045 | 40052 | 8 | R | 0x03 | Vr | SW version of | string |  |  | e.g. "2.9"
40053 | 40068 | 16 | R | 0x03 | SN | Smart Meter Serialnumber | string |  |  | e.g. "18370117"
40069 | 40069 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40070 | 40070 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model ac_meter (21x) | uint16 |  |  | 211: Single Phase (AN or AB), 212: Split Single Phase (ABN), 213: WYE-Connect Three Phase (ABCN), 214: Delta-Connect Three Phase (ABC)
40071 | 40071 | 1 | R | 0x03 | L | Length of sunspec model ac_meter (21x) | uint16 | Registers |  | 124
40072 | 40073 | 2 | R | 0x03 | A | Total AC Current | float32 | A
40074 | 40075 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
40076 | 40077 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
40078 | 40079 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
40080 | 40081 | 2 | R | 0x03 | PhV | Line to Neutral AC Voltage (average of active phases) | float32 | V
40082 | 40083 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
40084 | 40085 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40086 | 40087 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40088 | 40089 | 2 | R | 0x03 | PPV | Line to Line AC Voltage (average of active phases) | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40090 | 40091 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40092 | 40093 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40094 | 40095 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
40096 | 40097 | 2 | R | 0x03 | Hz | Frequency | float32 | Hz
40098 | 40099 | 2 | R | 0x03 | W | Total Real Power | float32 | W
40100 | 40101 | 2 | R | 0x03 | WphA | Watts phase A | float32 | W
40102 | 40103 | 2 | R | 0x03 | WphB | Watts phase B | float32 | W |  | This data-point is supported/not-supported depending on the grid connection.
40104 | 40105 | 2 | R | 0x03 | WphC | Watts phase C | float32 | W |  | This data-point is supported/not-supported depending on the grid connection.
40106 | 40107 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
40108 | 40109 | 2 | R | 0x03 | VAphA | VA phase A | float32 | VA
40110 | 40111 | 2 | R | 0x03 | VAphB | VA phase B | float32 | VA |  | This data-point is supported/not-supported depending on the grid connection.
40112 | 40113 | 2 | R | 0x03 | VAphC | VA phase C | float32 | VA |  | This data-point is supported/not-supported depending on the grid connection.
40114 | 40115 | 2 | R | 0x03 | VAR | Reactive Power | float32 | var
40116 | 40117 | 2 | R | 0x03 | VARphA | VAR phase A | float32 | var
40118 | 40119 | 2 | R | 0x03 | VARphB | VAR phase B | float32 | var |  | This data-point is supported/not-supported depending on the grid connection.
40120 | 40121 | 2 | R | 0x03 | VARphC | VAR phase C | float32 | var |  | This data-point is supported/not-supported depending on the grid connection.
40122 | 40123 | 2 | R | 0x03 | PF | Power Factor | float32 | PF
40124 | 40125 | 2 | R | 0x03 | PFphA | PF phase A | float32 | PF
40126 | 40127 | 2 | R | 0x03 | PFphB | PF phase B | float32 | PF |  | This data-point is supported/not-supported depending on the grid connection.
40128 | 40129 | 2 | R | 0x03 | PFphC | PF phase C | float32 | PF |  | This data-point is supported/not-supported depending on the grid connection.
40130 | 40131 | 2 | R | 0x03 | TotWhExp | Total Real Energy Exported | float32 | Wh
40132 | 40133 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | float32 | Wh
40134 | 40135 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
40136 | 40137 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
40138 | 40139 | 2 | R | 0x03 | TotWhImp | Total Real Energy Imported | float32 | Wh
40140 | 40141 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | float32 | Wh
40142 | 40143 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
40144 | 40145 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
40146 | 40147 | 2 | R | 0x03 | TotVAhExp | Total Apparent Energy Exported | float32 | VAh
40148 | 40149 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | float32 | VAh
40150 | 40151 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
40152 | 40153 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
40154 | 40155 | 2 | R | 0x03 | TotVAhImp | Total Apparent Energy Imported | float32 | VAh
40156 | 40157 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | float32 | VAh
40158 | 40159 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
40160 | 40161 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
40162 | 40163 | 2 | R | 0x03 | TotVArhImpQ1 | Total Reactive Energy Imported Quadrant 1 | float32 | varh |  | not supported
40164 | 40165 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAr-hours Imported Q1 phase A | float32 | varh |  | not supported
40166 | 40167 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAr-hours Imported Q1 phase B | float32 | varh |  | not supported
40168 | 40169 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAr-hours Imported Q1 phase C | float32 | varh |  | not supported
40170 | 40171 | 2 | R | 0x03 | TotVArhImpQ2 | Total Reactive Power Imported Quadrant 2 | float32 | varh |  | not supported
40172 | 40173 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAr-hours Imported Q2 phase A | float32 | varh |  | not supported
40174 | 40175 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAr-hours Imported Q2 phase B | float32 | varh |  | not supported
40176 | 40177 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAr-hours Imported Q2 phase C | float32 | varh |  | not supported
40178 | 40179 | 2 | R | 0x03 | TotVArhExpQ3 | Total Reactive Power Exported Quadrant 3 | float32 | varh |  | not supported
40180 | 40181 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAr-hours Exported Q3 phase A | float32 | varh |  | not supported
40182 | 40183 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAr-hours Exported Q3 phase B | float32 | varh |  | not supported
40184 | 40185 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAr-hours Exported Q3 phase C | float32 | varh |  | not supported
40186 | 40187 | 2 | R | 0x03 | TotVArhExpQ4 | Total Reactive Power Exported Quadrant 4 | float32 | varh |  | not supported
40188 | 40189 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAr-hours Exported Q4 Imported phase A | float32 | varh |  | not supported
40190 | 40191 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAr-hours Exported Q4 Imported phase B | float32 | varh |  | not supported
40192 | 40193 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAr-hours Exported Q4 Imported phase C | float32 | varh |  | not supported
40194 | 40195 | 2 | R | 0x03 | Evt | Meter Event Flags | bitfield32 |  |  | currently hardcoded to zero
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
40196 | 40196 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
40197 | 40197 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0

## common (1)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model common (1) | uint16 |  |  | 1
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model common (1) | uint16 | Registers |  | 65
3 | 18 | 16 | R | 0x03 | Mn | Smart Meter Manufacturer | string |  |  | e.g. "Fronius"
19 | 34 | 16 | R | 0x03 | Md | Smart Meter Model | string |  |  | e.g. "Smart Meter 63A"
35 | 42 | 8 | R | 0x03 | Opt | Smart Meter Name | string |  |  | e.g. "<primary>"
43 | 50 | 8 | R | 0x03 | Vr | SW version of | string |  |  | e.g. "2.9"
51 | 66 | 16 | R | 0x03 | SN | Smart Meter Serialnumber | string |  |  | e.g. "18370117"
67 | 67 | 1 | R | 0x03 | DA | Modbus Device Address | uint16 |  |  | 1 - 247

## ac_meter (21x)
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Well-known value. Uniquely identifies this as a sunspec model ac_meter (21x) | uint16 |  |  | 211: Single Phase (AN or AB), 212: Split Single Phase (ABN), 213: WYE-Connect Three Phase (ABCN), 214: Delta-Connect Three Phase (ABC)
2 | 2 | 1 | R | 0x03 | L | Length of sunspec model ac_meter (21x) | uint16 | Registers |  | 124
3 | 4 | 2 | R | 0x03 | A | Total AC Current | float32 | A
5 | 6 | 2 | R | 0x03 | AphA | Phase A Current | float32 | A
7 | 8 | 2 | R | 0x03 | AphB | Phase B Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
9 | 10 | 2 | R | 0x03 | AphC | Phase C Current | float32 | A |  | This data-point is supported/not-supported depending on the grid connection.
11 | 12 | 2 | R | 0x03 | PhV | Line to Neutral AC Voltage (average of active phases) | float32 | V
13 | 14 | 2 | R | 0x03 | PhVphA | Phase Voltage AN | float32 | V
15 | 16 | 2 | R | 0x03 | PhVphB | Phase Voltage BN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
17 | 18 | 2 | R | 0x03 | PhVphC | Phase Voltage CN | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
19 | 20 | 2 | R | 0x03 | PPV | Line to Line AC Voltage (average of active phases) | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
21 | 22 | 2 | R | 0x03 | PPVphAB | Phase Voltage AB | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
23 | 24 | 2 | R | 0x03 | PPVphBC | Phase Voltage BC | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
25 | 26 | 2 | R | 0x03 | PPVphCA | Phase Voltage CA | float32 | V |  | This data-point is supported/not-supported depending on the grid connection.
27 | 28 | 2 | R | 0x03 | Hz | Frequency | float32 | Hz
29 | 30 | 2 | R | 0x03 | W | Total Real Power | float32 | W
31 | 32 | 2 | R | 0x03 | WphA | Watts phase A | float32 | W
33 | 34 | 2 | R | 0x03 | WphB | Watts phase B | float32 | W |  | This data-point is supported/not-supported depending on the grid connection.
35 | 36 | 2 | R | 0x03 | WphC | Watts phase C | float32 | W |  | This data-point is supported/not-supported depending on the grid connection.
37 | 38 | 2 | R | 0x03 | VA | AC Apparent Power | float32 | VA
39 | 40 | 2 | R | 0x03 | VAphA | VA phase A | float32 | VA
41 | 42 | 2 | R | 0x03 | VAphB | VA phase B | float32 | VA |  | This data-point is supported/not-supported depending on the grid connection.
43 | 44 | 2 | R | 0x03 | VAphC | VA phase C | float32 | VA |  | This data-point is supported/not-supported depending on the grid connection.
45 | 46 | 2 | R | 0x03 | VAR | Reactive Power | float32 | var
47 | 48 | 2 | R | 0x03 | VARphA | VAR phase A | float32 | var
49 | 50 | 2 | R | 0x03 | VARphB | VAR phase B | float32 | var |  | This data-point is supported/not-supported depending on the grid connection.
51 | 52 | 2 | R | 0x03 | VARphC | VAR phase C | float32 | var |  | This data-point is supported/not-supported depending on the grid connection.
53 | 54 | 2 | R | 0x03 | PF | Power Factor | float32 | PF
55 | 56 | 2 | R | 0x03 | PFphA | PF phase A | float32 | PF
57 | 58 | 2 | R | 0x03 | PFphB | PF phase B | float32 | PF |  | This data-point is supported/not-supported depending on the grid connection.
59 | 60 | 2 | R | 0x03 | PFphC | PF phase C | float32 | PF |  | This data-point is supported/not-supported depending on the grid connection.
61 | 62 | 2 | R | 0x03 | TotWhExp | Total Real Energy Exported | float32 | Wh
63 | 64 | 2 | R | 0x03 | TotWhExpPhA | Total Watt-hours Exported phase A | float32 | Wh
65 | 66 | 2 | R | 0x03 | TotWhExpPhB | Total Watt-hours Exported phase B | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
67 | 68 | 2 | R | 0x03 | TotWhExpPhC | Total Watt-hours Exported phase C | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
69 | 70 | 2 | R | 0x03 | TotWhImp | Total Real Energy Imported | float32 | Wh
71 | 72 | 2 | R | 0x03 | TotWhImpPhA | Total Watt-hours Imported phase A | float32 | Wh
73 | 74 | 2 | R | 0x03 | TotWhImpPhB | Total Watt-hours Imported phase B | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
75 | 76 | 2 | R | 0x03 | TotWhImpPhC | Total Watt-hours Imported phase C | float32 | Wh |  | This data-point is supported/not-supported depending on the grid connection.
77 | 78 | 2 | R | 0x03 | TotVAhExp | Total Apparent Energy Exported | float32 | VAh
79 | 80 | 2 | R | 0x03 | TotVAhExpPhA | Total VA-hours Exported phase A | float32 | VAh
81 | 82 | 2 | R | 0x03 | TotVAhExpPhB | Total VA-hours Exported phase B | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
83 | 84 | 2 | R | 0x03 | TotVAhExpPhC | Total VA-hours Exported phase C | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
85 | 86 | 2 | R | 0x03 | TotVAhImp | Total Apparent Energy Imported | float32 | VAh
87 | 88 | 2 | R | 0x03 | TotVAhImpPhA | Total VA-hours Imported phase A | float32 | VAh
89 | 90 | 2 | R | 0x03 | TotVAhImpPhB | Total VA-hours Imported phase B | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
91 | 92 | 2 | R | 0x03 | TotVAhImpPhC | Total VA-hours Imported phase C | float32 | VAh |  | This data-point is supported/not-supported depending on the grid connection.
93 | 94 | 2 | R | 0x03 | TotVArhImpQ1 | Total Reactive Energy Imported Quadrant 1 | float32 | varh |  | not supported
95 | 96 | 2 | R | 0x03 | TotVArhImpQ1phA | Total VAr-hours Imported Q1 phase A | float32 | varh |  | not supported
97 | 98 | 2 | R | 0x03 | TotVArhImpQ1phB | Total VAr-hours Imported Q1 phase B | float32 | varh |  | not supported
99 | 100 | 2 | R | 0x03 | TotVArhImpQ1phC | Total VAr-hours Imported Q1 phase C | float32 | varh |  | not supported
101 | 102 | 2 | R | 0x03 | TotVArhImpQ2 | Total Reactive Power Imported Quadrant 2 | float32 | varh |  | not supported
103 | 104 | 2 | R | 0x03 | TotVArhImpQ2phA | Total VAr-hours Imported Q2 phase A | float32 | varh |  | not supported
105 | 106 | 2 | R | 0x03 | TotVArhImpQ2phB | Total VAr-hours Imported Q2 phase B | float32 | varh |  | not supported
107 | 108 | 2 | R | 0x03 | TotVArhImpQ2phC | Total VAr-hours Imported Q2 phase C | float32 | varh |  | not supported
109 | 110 | 2 | R | 0x03 | TotVArhExpQ3 | Total Reactive Power Exported Quadrant 3 | float32 | varh |  | not supported
111 | 112 | 2 | R | 0x03 | TotVArhExpQ3phA | Total VAr-hours Exported Q3 phase A | float32 | varh |  | not supported
113 | 114 | 2 | R | 0x03 | TotVArhExpQ3phB | Total VAr-hours Exported Q3 phase B | float32 | varh |  | not supported
115 | 116 | 2 | R | 0x03 | TotVArhExpQ3phC | Total VAr-hours Exported Q3 phase C | float32 | varh |  | not supported
117 | 118 | 2 | R | 0x03 | TotVArhExpQ4 | Total Reactive Power Exported Quadrant 4 | float32 | varh |  | not supported
119 | 120 | 2 | R | 0x03 | TotVArhExpQ4phA | Total VAr-hours Exported Q4 Imported phase A | float32 | varh |  | not supported
121 | 122 | 2 | R | 0x03 | TotVArhExpQ4phB | Total VAr-hours Exported Q4 Imported phase B | float32 | varh |  | not supported
123 | 124 | 2 | R | 0x03 | TotVArhExpQ4phC | Total VAr-hours Exported Q4 Imported phase C | float32 | varh |  | not supported
125 | 126 | 2 | R | 0x03 | Evt | Meter Event Flags | bitfield32 |  |  | currently hardcoded to zero

## End Block
Start | End | Size | R/W | Function codes | Name | Description | Type | Units | Scale Factor | Range of values
1 | 1 | 1 | R | 0x03 | ID | Identifies this as End block | uint16 |  |  | 0xFFFF
2 | 2 | 1 | R | 0x03 | L | Length of model block | uint16 |  |  | 0x0